## Buses
bus_id2 | bus_id | name | vn_kv | geodata | bus type | Trafo?
0 | 0 | Ibiza (+ Formentura) | 132 | (1.430833, 38.91917) | gen/load | N
1l | 1 | Santa Ponca (132) | 132 | (2.506454, 39.53525) | load | Y, LV
1h | 2 | Santa Ponca (220) | 220 | (2.507937, 39.53662) | ext_grid | Y, HV
2 | 3 | Valldurgent | 220 | (2.549167, 39.58417) | load | N
3 | 4 | Son Reus | 220 | (2.678889, 39.65083) | gen/load | N
4h | 5 | Portol (Cas Tresorer) (220) | 220 | (2.724617, 39.56686) | gen | Y, HV
4l | 6 | Portol (Cas Tresorer) (66) | 66 | (2.724617, 39.56686) | load | Y, LV
5 | 7 | Son Orlandis | 220 | (2.744444, 39.60028) | load | N
6 | 8 | Llubi | 220 | (3.039444, 39.67333) | load | N
7 | 9 | Murterar | 220 | (3.0925, 39.80944) | load/gen | N
8h | 10 | Es Bessons (220) | 220 | (3.158056, 39.58194) | bus | Y, HV
8l | 11 | Es Bessons (132) | 132 | (3.159638, 39.58209) | load | N, LV
9 | 12 | Cala Mesquida | 132 | (3.427024, 39.73827) | load | N
10 | 13 | Cala en Bosch | 132 | (3.834227, 39.93175) | load | N
11 | 14 | Cuitadella | 132 | (3.855278, 40.00333) | load | N
12 | 15 | Es Mercadal | 132 | (4.095556, 39.97694) | load | N
13 | 16 | Dragonera | 132 | (4.236667, 39.89111) | load | N
14 | 17 | Mao | 132 | (4.258155, 39.89706) | gen/load | N

## Loads
Location | bus_id2 | bus_id | name | vn_kv | population | demand_share | summer_p_mw | summer_q_mvar | summer_s | winter_p_mw | winter_q_mvar | winter_s
Ibiza | 0 | 0 | Ibiza (+ Formentura) | 132 | 160000 | 0.1346 | 175.4296 | 84.9644 | 194.9218 | 128.7112 | 62.3377 | 143.0124
Majorca | 1l | 1 | Santa Ponsa (132) | 132 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 2 | 3 | Valldurgent | 220 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 3 | 4 | Son Reus | 220 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 4l | 6 | Portol (Cas Tresorer) (66) | 66 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 5 | 7 | Son Orlandis | 220 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 6 | 8 | Llubi | 220 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 7 | 9 | Murterar | 220 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 8l | 11 | Es Bessons (132) | 132 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 9 | 12 | Cala Mesquida | 132 | 103111 | 0.0868 | 113.0546 | 54.7549 | 125.6163 | 82.9472 | 40.1732 | 92.1636
Majorca | 10 | 13 | Cala en Bosch | 132 | 7000 | 0.0059 | 7.675 | 3.7172 | 8.5278 | 5.6311 | 2.7273 | 6.2568
Minorca | 11 | 14 | Cuitadella | 132 | 29840 | 0.0251 | 32.7176 | 15.8459 | 36.3529 | 24.0046 | 11.626 | 26.6718
Minorca | 12 | 15 | Es Mercadal | 132 | 20285 | 0.0171 | 22.2412 | 10.7719 | 24.7124 | 16.3182 | 7.9032 | 18.1313
Minorca | 13 | 16 | Dragonera | 132 | 14232 | 0.012 | 15.6045 | 7.5576 | 17.3383 | 11.4489 | 5.5449 | 12.721
Minorca | 14 | 17 | Mao | 132 | 29040 | 0.0244 | 31.8405 | 15.421 | 35.3783 | 23.3611 | 11.3143 | 25.9568

## Generators
island | name | bus_connection | capacity_mw | actual_gen_pro_rata | pro_rata_gen | Geodata
Ibiza+Fomentera | Elvissa+Saint Francesco | 0 | 306 | 230.7 | 208.6436 | (38.919167, 1.430833)
Mallorca | Son Reus | 4 | 432.8 | 303.0173 | 295.1012 | (39.648611, 2.680000)
Mallorca | Cas Tresorer | 5 | 400 | 280.0529 | 272.7368 | (39.567500, 2.689444)
Mallorca | Murterar | 9 | 527.8 | 369.5298 | 359.8762 | (39.809722, 3.091944)
Menorca | Mahon (Mao) | 17 | 245 | 113.2 | 167.0513 | (39.896944, 4.258611)

## Lines
index | from_bus | to_bus | length_km | cable_type | bundle_no | Dm | A | Rb | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | max_i_ka | cables | voltage | location
1 | 0 | 1 | 126 | Biggest |  |  | 500 |  | 0.042063 | 0.11618 | 2.1e-09 | 0.6 | 1 | 132 | underwater
2 | 2 | 3 | 5.5997 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
3 | 3 | 4 | 15.0251 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
4 | 3 | 4 | 14.8977 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
5 | 4 | 7 | 9.4179 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
6 | 4 | 8 | 33.8304 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
7 | 7 | 5 | 4.3577 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
8 | 7 | 8 | 28.9062 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
9 | 8 | 9 | 16.7702 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
10 | 8 | 9 | 16.0636 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
11 | 8 | 10 | 15.1772 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
12 | 8 | 10 | 14.9541 | Condor | 2 | 11 | 402.3 | 0.06639 | 0.024277 | 0.32108 | 1e-09 | 0.975 | 3 | 220 | overhead
13 | 11 | 12 | 30.2764 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead
14 | 12 | 13 | 52.942 | Biggest |  |  | 630 |  | 0.042063 | 0.11618 | 2.1e-09 | 0.6 | 1 | 132 | underwater
15 | 13 | 14 | 8.2014 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead
16 | 14 | 16 | 35.5456 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead
17 | 14 | 15 | 21.1322 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead
18 | 15 | 16 | 15.4394 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead
19 | 16 | 17 | 4.7127 | Condor | 2 | 8.75 | 402.3 | 0.06639 | 0.024277 | 0.3067 | 1e-09 | 0.975 | 3 | 132 | overhead

## Changing line values
cable used: |  | Area | Resistance at 25 | Inductance | Capacitance | max_i_ka | type
page 4, Condor from :https://www.elandcables.com/media/38193/acsr-astm-b-aluminium-conductor-steel-reinforced.pdf | OVERHEAD | 402.3 | 0.07283 | N/A | 1e-09 | 0.975 | Condor
page 8, Table 48, :https://new.abb.com/docs/default-source/ewea-doc/xlpe-submarine-cable-systems-2gm5007.pdf | MARINE | 630 | N/A | 0.37 | 2.1e-09 | 0.6
Note: capacitance for overheads is assumed, just use that for all of them, he is not even asking for it in the tables | note: for marine cable we used a 150kv cable rather than 132 for safety

## Generation profile
Summer
Majorca | 952.6
Minorca | 113.2
Ibiza | 218.7
Formantera | 12
Total | 1297.4
Winter
Majorca | 738.6
Minorca | 64.6
Ibiza | 134.8
Formantera | 7.8
Total | 945.8